## Slide 1: IEC 61850 Data Modelling for Utilities
PAC World Americas Conference 2020
Jörg Reuter, Helinks LLC, Giuseppe Rigadello Enyr SRL 1.09.2020
jr@helinks.com, giuseppe.rigadello@enyr.eu

## Slide 2: IEC 61850 Data Modeling for Utilities
What is an IEC 61850 Data Model?
Why Utilities care about IEC 61850 Data Modeling ?
How to create an IEC 61850 Data Model?
Conclusion!

## Slide 3: Reminder :Content of SCL Files
Network(s)
Substation
Voltage Level
Bay
Function
Logical Node (LNode)
IED
Logical Device
Communication Configuration
Logical Node (LN)
Logical Node Type
Data Object Type
Data Attribute Type
Enum Type
SubNet
IED AP
IED AP
IP Address Params
Communication Params
Process or Substation
Section
Data Type
Templates
Section
IED
Section
Communication
Section

## Slide 4: SCL and NSD Files
Logical Node Type
Data Object Type
Data Attribute Type
Enum Type
IEC 61850-7-4
Word or PDF
Code Component
NSD Files: Name Space Description
SCL Data Type Templates

## Slide 5
IED Manufacturer
ICD File
Utility
System Integrator
Informal
System Specification
Vendor Data
Types
Private Vendor Namespace
IEC 61850
7-2/3/4
SCD File
Vendor
Data
Model
Different solutions for similar Substations/Generation Facilities
No drawings for Application Schemes
Hard to understand for the customer
Nearly impossible to maintain
System Integrator takes
application design decisions and makes
data selection and IEC 61850 mapping

## Slide 6
IED Manufacturer
Utility
System Integrator
SSD/ISD File
Utility
Data
Model
Utility takes
application design decisions and makes
data selection and IEC 61850 mapping
Customized ICD File
Utility
Data
Model
Customized
Mappings
ICD File
Vendor Data
Model
SCD File
Utility Driven
Data Model
Private Utility Namespace
IEC 61850
7-2/3/4
Deep IEC 61850 Expertise needed

## Slide 7: Definition
IEC 61850 Namespaces are structured collections of Logical Nodes (LN), Data Objects and potentially Common Data Classes (CDC) and Data Attributes.
They provide the basic building blocks for Data Type Template sections in SCL File.
Namespaces are stored in NSD files (XML).
IEC DTS 61850-1-2 © IEC 2019
…and the relevant IEC Standardization document

## Slide 8: Namespace Definition for Utilities
IEC 61850 Basic Namespaces
contain the basic classes from which all other namespaces are built, e.g. IEC 61850-7-2; IEC 61850-7-3; IEC 61850-7-4.
IEC 61850 Domain Namespaces
Namespace which extends IEC 61850 covering a specific application domain. E.g. parts 7-4xx
IEC 61850 Product Namespace
Namespace focussing on Products like Switchgear or IEDs and adding specific information about the product via detailed nameplate information.
IEC 61850 Private Namespace
private data model namespace which extends IEC 61850 with the purpose of better supporting a private implementation(IED vendor) or specification (Utility) of IEC 61850.
IEC 61850 transitional namespace
data model namespace which has the goal to expose a proposed extension of the data model to the market, before being formally embedded into a standard (product, domain or basic) namespace
Source: IEC DTS 61850-1-2 © IEC 2019

## Slide 9: Properties of Namespaces
Ownership
A Namespace has an owner who is responsible for the definition and maintenance of the Namespace
Traceability
Objects can indicate on which Namespace they are based on.
Inheritance
Namespaces can be chained together
Rules
Strict rules for the definition and extension of Namespaces prevent owners from jeopardizing interoperability.
Identification
Namespaces are identified by a Name,Version Release and the dependency to other Namespaces
Source: IEC DTS 61850-1-2 © IEC 2019

## Slide 10: Rules for the definition of Namespaces
Operation | Rule for Private Namespace Definition
Data Model | 
Extending existing LNs with new DOs | Allowed following DO naming rules within the scope of the product functions
Create new LNs | Allowed following LN/DO naming rules within the scope of the product functions
Deprecate existing LNs | Allowed only by the owner of the namespace
Extending existing DOs enumeration | Allowed under specific conditions and a specific process
Extending CDC with new attributes (DA) | Forbidden
Create a new CDC | Forbidden
Extending existing DAs enumeration | Forbidden
Making more stringent the DO presence conditions on existing LNs | This DO should be tagged as “namespace specific”
Making less stringent the DO presence conditions on existing LNs | Forbidden
Deprecating DOs from existing LNs | Allowed
Making more stringent the DA presence conditions on existing LNs | In some very specific cases
Making less stringent the DA presence conditions | Forbidden
Defining rules for LN prefix/suffix | Forbidden
Defining rules for LD arrangements | Forbidden
Communication services | 
Extending the ACSI | Forbidden
Providing a new SCSM | Forbidden
SCL language | 
Extending the SCL grammar (XSD) with SCL new tags and new attributes | Forbidden
Extending the SCL grammar (XSD) through private sections | Allowed
Extending the SCL grammar (XSD) with tags and new attributes from other xml namespace | Allowed
Source: IEC DTS 61850-1-2 © IEC 2019

## Slide 11: Process
IEC 61850
7-2/3/4
IEC 61850
7-4xx
Private Utility
Namespace
ISD File
Utility
Data
Model
SSD File
Utility
Data
Model
Utility Model Manager defines the Private Utility Namespace by
Inheriting Definitions from Base- and Domain Namespaces
Selecting a subset of elements
Extending certain elements
Utilities negotiate Frame Agreements with vendors based on ISD files that are based on the Private Utility Namespace
Utilities issue System Specifications for Substations or Generation Facilities (SSD files) that are based on the Private Utility Namespace
Build up IEC 61850 competence.
Define a Data Model Manager in your organization.
Use IEC 61850 tools for the modeling work.
Embed the Utility Data Model in the company processes.

## Slide 12: The Benefits of Standardisation
System Specification
Template Definition
System Integration
IED
Configuration Tool
PDIS
IED
System
Specification
Tool
IED
Configuration Tool
PDIS
IED
Engineering
Template
System
Integration
Tool
System
Specification
System
Specification
Tool
System
Integration
Tool
System
Configuration
Utility driven
Data Model
Utility driven
Data Model
Utility driven
Data Model

## Slide 13: Conclusion
Utilities stay in control of the design of their applications and systems.
Similar Substations/ Generation Facilties have similar designs.
Maintenance is feasible with reasonable effort.
PAC projects can be run more efficiently.
There is no “Free Lunch”. Building up IEC 61850 knowledge requires an effort.
IEC 61850 has a steep learning curve.
Do not shy away from using consultants for initial support
Utility Namespace

## Slide 14
For feedback or questions:
jr@helinks.com
giuseppe.rigadello@enyr.eu